## BoQ for first 2 years
Establishment of Long Term Arrangement (LTA) for Provision of Rehabilitation and Construction Implementation Services for Education, Health and Nutrition, and WASH Sectors in Türkiye and Syria 6 (2+2+2) years (2025-05/LRPS#9195663) Rehabilitation and Modernization of Health & Nutrition Centers - First 2 Years
This project focuses on the comprehensive rehabilitation and modernization of healthcare centers to enhance functionality, safety, and accessibility for patients and staff. The project addresses critical structural repairs, accessibility upgrades, and improvements in plumbing, electrical, and HVAC systems to ensure compliance with modern safety and operational standards. It also incorporates sustainable and energy-efficient solutions, such as LED smart lighting and solar-powered systems, to reduce operational costs and environmental impact. Special emphasis is placed on the renovation of laboratory and diagnostic areas, the installation of biohazard waste management systems, and the introduction of advanced wastewater treatment solutions to maintain hygiene and environmental compliance. Landscaping and outdoor area improvements aim to provide a welcoming environment for patients and visitors. The project also includes detailed documentation and reporting for compliance and stakeholder engagement, ensuring transparency and accountability. By modernizing these healthcare facilities, the project aims to improve service delivery, enhance patient safety, and create a sustainable and efficient healthcare infrastructure capable of meeting growing demands in Syria and Türkiye.
Ref. | Goods / Services | Description / Specifications | Unit | Quantity | Unit Cost US$ | Unit Cost US$ | Total Cost US$ | Total Cost US$
[5 empty] | Syria | Türkiye | Syria | Türkiye
A21 | Wall and Roof Repairs | Restoration of 1,500 m² of walls using M20-grade concrete and polymer-modified waterproof coatings. Replacement of 1,200 m² of roof sheets with pre-painted galvanized steel (0.5 mm thick) along with a vapor barrier. Structural reinforcement of 15 roof trusses using MS angles. Roof gutter repairs include installation of 100 meters of uPVC gutters for rainwater drainage. | Lump sum | 1
U21 | Structural Repairs | Strengthening of 20 columns and 15 beams with M30-grade concrete jacketing (50 mm thickness) using shuttering and injection grouting. Replacement of corroded rebar with Fe500 TMT rebars. Epoxy crack injection is included to seal 50 m of foundation cracks. Anchoring plates and bolts are used for beam-column connections to improve structural integrity. | Lump sum | 1
A23 | Accessibility Enhancements | Construction of 5 wheelchair ramps, each 2 m wide and complying with ADA standards (1:12 slope). Ramps include non-slip epoxy finishes and tactile indicators. Installation of 100 meters of stainless-steel handrails (38 mm diameter). Includes 150 m² of tactile paving for visually impaired persons. Two wheelchair-accessible lifts (ISO 9386 compliant) with a capacity of 500 kg are also provided. | Lump sum | 1
A22 | Utility System Upgrades | Replacement of 200 meters of old plumbing with CPVC (Sch 40) pipes for cold water and insulated PPR pipes for hot water. Installation of two 5,000 L water tanks made of HDPE on reinforced concrete platforms. Electrical upgrades for 80 rooms, including replacement of light fixtures with 40W LED lights and installation of a 10-ton split HVAC system with R410A refrigerant for energy efficiency. | Lump sum | 1
A24 | Interior Refurbishment | Replacement of 2,000 m² of flooring with anti-slip, anti-bacterial vinyl tiles (3 mm thick). Painting of 1,800 m² of walls with low-VOC, antimicrobial paint (two coats). Installation of 50 modular seating units with upholstered cushioning for outpatient areas. Replacement of 15 wooden doors with fire-rated doors (30-minute resistance) including durable hinges and locking systems. | Lump sum | 1
P23 | Plumbing Upgrades | Replacement of 150 m of damaged sewer lines with uPVC pipes (200 mm diameter). Includes construction of 5 precast RCC manholes (1.2 m diameter) and replacement of two septic tanks (5 m³ capacity) with prefabricated FRP units. Hydro-testing of pipelines is conducted at 3 bar pressure for leak-proof performance. Proper alignment and slope (1%) are ensured for sewer flow. | Lump sum | 1
P26 | Internal Coatings for Wet Areas | Application of epoxy waterproof coatings (3 mm thick) to 500 m² of wet areas, including treatment rooms, restrooms, and washing zones. Includes joint sealing with polyurethane for long-term durability. The work also involves surface preparation with grinding and application of a primer coat for adherence. | Lump sum | 1
A26 | Outdoor Area Improvements | Rehabilitation of 200 meters of pathways with 60 mm thick concrete tiles (anti-slip surface). Landscaping of 500 m², including planting of native shrubs and grass. Installation of 10 outdoor solar-powered LED lights (30W, pole height: 6 m) and two steel benches with anti-corrosion paint finishes for outdoor seating. | Lump sum | 1
A210 | Waste Management Systems | Installation of 3 color-coded biohazard waste bins (120 L capacity each) for proper segregation (red, yellow, and black bins) with clear signage. Transportation and disposal of construction debris (estimated 10 tons) to certified waste facilities. Includes provision of PPE for workers handling biohazard materials, ensuring compliance with WHO guidelines for medical waste management. | Lump sum | 1
A28 | Laboratory and Diagnostic Area Upgrade | Refurbishment of 150 m² of laboratory space, including installation of chemical-resistant epoxy flooring (4 mm thick). Fabrication and installation of epoxy-coated steel countertops (10 m total length) with integrated sinks (5 units, stainless steel, 600 mm x 450 mm). Electrical modifications include five new power outlets with surge protection and upgraded earthing for sensitive equipment. | Lump sum | 1
P36 | UV Disinfection System for Wastewater | Installation of a UV-based wastewater treatment system with a capacity of 10 m³/day. The system includes UV lamps (254 nm wavelength) housed in stainless steel chambers, control panels, and an auto-cleaning mechanism. Includes testing and commissioning to ensure treated water meets WHO discharge standards for biological contamination (<10 CFU/mL). | Lump sum | 1
G54 | Energy-Efficient Smart Lighting Systems | Installation of 60 smart LED light units, each with 20W power and motion sensors for occupancy-based control. Daylight dimmers are integrated for energy efficiency. The system complies with IEC 60598 standards for safety and performance. Includes replacement of old wiring and installation of fire-resistant conduits for safe operation. | Lump sum | 1
S814 | Final Reporting and Closeout | Preparation of as-built drawings (AutoCAD format), detailing all structural, mechanical, and electrical systems. Development of comprehensive O&M manuals for installed systems. Final project report includes challenges faced, resolutions, and compliance certifications. Stakeholder approvals for project handover are included. | Lump sum | 1

## BoQ for additional 2 years
Establishment of Long Term Arrangement (LTA) for Provision of Rehabilitation and Construction Implementation Services for Education, Health and Nutrition, and WASH Sectors in Türkiye and Syria 6 (2+2+2) years (2025-05/LRPS#9195663) Rehabilitation and Modernization of Health & Nutrition Centers - Additional 2 Years
This project focuses on the comprehensive rehabilitation and modernization of healthcare centers to enhance functionality, safety, and accessibility for patients and staff. The project addresses critical structural repairs, accessibility upgrades, and improvements in plumbing, electrical, and HVAC systems to ensure compliance with modern safety and operational standards. It also incorporates sustainable and energy-efficient solutions, such as LED smart lighting and solar-powered systems, to reduce operational costs and environmental impact. Special emphasis is placed on the renovation of laboratory and diagnostic areas, the installation of biohazard waste management systems, and the introduction of advanced wastewater treatment solutions to maintain hygiene and environmental compliance. Landscaping and outdoor area improvements aim to provide a welcoming environment for patients and visitors. The project also includes detailed documentation and reporting for compliance and stakeholder engagement, ensuring transparency and accountability. By modernizing these healthcare facilities, the project aims to improve service delivery, enhance patient safety, and create a sustainable and efficient healthcare infrastructure capable of meeting growing demands in Syria and Türkiye.
Ref. | Goods / Services | Description / Specifications | Unit | Quantity | Unit Cost US$ | Unit Cost US$ | Total Cost US$ | Total Cost US$
[5 empty] | Syria | Türkiye | Syria | Türkiye
A21 | Wall and Roof Repairs | Restoration of 1,500 m² of walls using M20-grade concrete and polymer-modified waterproof coatings. Replacement of 1,200 m² of roof sheets with pre-painted galvanized steel (0.5 mm thick) along with a vapor barrier. Structural reinforcement of 15 roof trusses using MS angles. Roof gutter repairs include installation of 100 meters of uPVC gutters for rainwater drainage. | Lump sum | 1
U21 | Structural Repairs | Strengthening of 20 columns and 15 beams with M30-grade concrete jacketing (50 mm thickness) using shuttering and injection grouting. Replacement of corroded rebar with Fe500 TMT rebars. Epoxy crack injection is included to seal 50 m of foundation cracks. Anchoring plates and bolts are used for beam-column connections to improve structural integrity. | Lump sum | 1
A23 | Accessibility Enhancements | Construction of 5 wheelchair ramps, each 2 m wide and complying with ADA standards (1:12 slope). Ramps include non-slip epoxy finishes and tactile indicators. Installation of 100 meters of stainless-steel handrails (38 mm diameter). Includes 150 m² of tactile paving for visually impaired persons. Two wheelchair-accessible lifts (ISO 9386 compliant) with a capacity of 500 kg are also provided. | Lump sum | 1
A22 | Utility System Upgrades | Replacement of 200 meters of old plumbing with CPVC (Sch 40) pipes for cold water and insulated PPR pipes for hot water. Installation of two 5,000 L water tanks made of HDPE on reinforced concrete platforms. Electrical upgrades for 80 rooms, including replacement of light fixtures with 40W LED lights and installation of a 10-ton split HVAC system with R410A refrigerant for energy efficiency. | Lump sum | 1
A24 | Interior Refurbishment | Replacement of 2,000 m² of flooring with anti-slip, anti-bacterial vinyl tiles (3 mm thick). Painting of 1,800 m² of walls with low-VOC, antimicrobial paint (two coats). Installation of 50 modular seating units with upholstered cushioning for outpatient areas. Replacement of 15 wooden doors with fire-rated doors (30-minute resistance) including durable hinges and locking systems. | Lump sum | 1
P23 | Plumbing Upgrades | Replacement of 150 m of damaged sewer lines with uPVC pipes (200 mm diameter). Includes construction of 5 precast RCC manholes (1.2 m diameter) and replacement of two septic tanks (5 m³ capacity) with prefabricated FRP units. Hydro-testing of pipelines is conducted at 3 bar pressure for leak-proof performance. Proper alignment and slope (1%) are ensured for sewer flow. | Lump sum | 1
P26 | Internal Coatings for Wet Areas | Application of epoxy waterproof coatings (3 mm thick) to 500 m² of wet areas, including treatment rooms, restrooms, and washing zones. Includes joint sealing with polyurethane for long-term durability. The work also involves surface preparation with grinding and application of a primer coat for adherence. | Lump sum | 1
A26 | Outdoor Area Improvements | Rehabilitation of 200 meters of pathways with 60 mm thick concrete tiles (anti-slip surface). Landscaping of 500 m², including planting of native shrubs and grass. Installation of 10 outdoor solar-powered LED lights (30W, pole height: 6 m) and two steel benches with anti-corrosion paint finishes for outdoor seating. | Lump sum | 1
A210 | Waste Management Systems | Installation of 3 color-coded biohazard waste bins (120 L capacity each) for proper segregation (red, yellow, and black bins) with clear signage. Transportation and disposal of construction debris (estimated 10 tons) to certified waste facilities. Includes provision of PPE for workers handling biohazard materials, ensuring compliance with WHO guidelines for medical waste management. | Lump sum | 1
A28 | Laboratory and Diagnostic Area Upgrade | Refurbishment of 150 m² of laboratory space, including installation of chemical-resistant epoxy flooring (4 mm thick). Fabrication and installation of epoxy-coated steel countertops (10 m total length) with integrated sinks (5 units, stainless steel, 600 mm x 450 mm). Electrical modifications include five new power outlets with surge protection and upgraded earthing for sensitive equipment. | Lump sum | 1
P36 | UV Disinfection System for Wastewater | Installation of a UV-based wastewater treatment system with a capacity of 10 m³/day. The system includes UV lamps (254 nm wavelength) housed in stainless steel chambers, control panels, and an auto-cleaning mechanism. Includes testing and commissioning to ensure treated water meets WHO discharge standards for biological contamination (<10 CFU/mL). | Lump sum | 1
G54 | Energy-Efficient Smart Lighting Systems | Installation of 60 smart LED light units, each with 20W power and motion sensors for occupancy-based control. Daylight dimmers are integrated for energy efficiency. The system complies with IEC 60598 standards for safety and performance. Includes replacement of old wiring and installation of fire-resistant conduits for safe operation. | Lump sum | 1
S814 | Final Reporting and Closeout | Preparation of as-built drawings (AutoCAD format), detailing all structural, mechanical, and electrical systems. Development of comprehensive O&M manuals for installed systems. Final project report includes challenges faced, resolutions, and compliance certifications. Stakeholder approvals for project handover are included. | Lump sum | 1

## BoQ for last 2 years
Establishment of Long Term Arrangement (LTA) for Provision of Rehabilitation and Construction Implementation Services for Education, Health and Nutrition, and WASH Sectors in Türkiye and Syria 6 (2+2+2) years (2025-05/LRPS#9195663) Rehabilitation and Modernization of Health & Nutrition Centers - Last 2 Years
This project focuses on the comprehensive rehabilitation and modernization of healthcare centers to enhance functionality, safety, and accessibility for patients and staff. The project addresses critical structural repairs, accessibility upgrades, and improvements in plumbing, electrical, and HVAC systems to ensure compliance with modern safety and operational standards. It also incorporates sustainable and energy-efficient solutions, such as LED smart lighting and solar-powered systems, to reduce operational costs and environmental impact. Special emphasis is placed on the renovation of laboratory and diagnostic areas, the installation of biohazard waste management systems, and the introduction of advanced wastewater treatment solutions to maintain hygiene and environmental compliance. Landscaping and outdoor area improvements aim to provide a welcoming environment for patients and visitors. The project also includes detailed documentation and reporting for compliance and stakeholder engagement, ensuring transparency and accountability. By modernizing these healthcare facilities, the project aims to improve service delivery, enhance patient safety, and create a sustainable and efficient healthcare infrastructure capable of meeting growing demands in Syria and Türkiye.
Ref. | Goods / Services | Description / Specifications | Unit | Quantity | Unit Cost US$ | Unit Cost US$ | Total Cost US$ | Total Cost US$
[5 empty] | Syria | Türkiye | Syria | Türkiye
A21 | Wall and Roof Repairs | Restoration of 1,500 m² of walls using M20-grade concrete and polymer-modified waterproof coatings. Replacement of 1,200 m² of roof sheets with pre-painted galvanized steel (0.5 mm thick) along with a vapor barrier. Structural reinforcement of 15 roof trusses using MS angles. Roof gutter repairs include installation of 100 meters of uPVC gutters for rainwater drainage. | Lump sum | 1
U21 | Structural Repairs | Strengthening of 20 columns and 15 beams with M30-grade concrete jacketing (50 mm thickness) using shuttering and injection grouting. Replacement of corroded rebar with Fe500 TMT rebars. Epoxy crack injection is included to seal 50 m of foundation cracks. Anchoring plates and bolts are used for beam-column connections to improve structural integrity. | Lump sum | 1
A23 | Accessibility Enhancements | Construction of 5 wheelchair ramps, each 2 m wide and complying with ADA standards (1:12 slope). Ramps include non-slip epoxy finishes and tactile indicators. Installation of 100 meters of stainless-steel handrails (38 mm diameter). Includes 150 m² of tactile paving for visually impaired persons. Two wheelchair-accessible lifts (ISO 9386 compliant) with a capacity of 500 kg are also provided. | Lump sum | 1
A22 | Utility System Upgrades | Replacement of 200 meters of old plumbing with CPVC (Sch 40) pipes for cold water and insulated PPR pipes for hot water. Installation of two 5,000 L water tanks made of HDPE on reinforced concrete platforms. Electrical upgrades for 80 rooms, including replacement of light fixtures with 40W LED lights and installation of a 10-ton split HVAC system with R410A refrigerant for energy efficiency. | Lump sum | 1
A24 | Interior Refurbishment | Replacement of 2,000 m² of flooring with anti-slip, anti-bacterial vinyl tiles (3 mm thick). Painting of 1,800 m² of walls with low-VOC, antimicrobial paint (two coats). Installation of 50 modular seating units with upholstered cushioning for outpatient areas. Replacement of 15 wooden doors with fire-rated doors (30-minute resistance) including durable hinges and locking systems. | Lump sum | 1
P23 | Plumbing Upgrades | Replacement of 150 m of damaged sewer lines with uPVC pipes (200 mm diameter). Includes construction of 5 precast RCC manholes (1.2 m diameter) and replacement of two septic tanks (5 m³ capacity) with prefabricated FRP units. Hydro-testing of pipelines is conducted at 3 bar pressure for leak-proof performance. Proper alignment and slope (1%) are ensured for sewer flow. | Lump sum | 1
P26 | Internal Coatings for Wet Areas | Application of epoxy waterproof coatings (3 mm thick) to 500 m² of wet areas, including treatment rooms, restrooms, and washing zones. Includes joint sealing with polyurethane for long-term durability. The work also involves surface preparation with grinding and application of a primer coat for adherence. | Lump sum | 1
A26 | Outdoor Area Improvements | Rehabilitation of 200 meters of pathways with 60 mm thick concrete tiles (anti-slip surface). Landscaping of 500 m², including planting of native shrubs and grass. Installation of 10 outdoor solar-powered LED lights (30W, pole height: 6 m) and two steel benches with anti-corrosion paint finishes for outdoor seating. | Lump sum | 1
A210 | Waste Management Systems | Installation of 3 color-coded biohazard waste bins (120 L capacity each) for proper segregation (red, yellow, and black bins) with clear signage. Transportation and disposal of construction debris (estimated 10 tons) to certified waste facilities. Includes provision of PPE for workers handling biohazard materials, ensuring compliance with WHO guidelines for medical waste management. | Lump sum | 1
A28 | Laboratory and Diagnostic Area Upgrade | Refurbishment of 150 m² of laboratory space, including installation of chemical-resistant epoxy flooring (4 mm thick). Fabrication and installation of epoxy-coated steel countertops (10 m total length) with integrated sinks (5 units, stainless steel, 600 mm x 450 mm). Electrical modifications include five new power outlets with surge protection and upgraded earthing for sensitive equipment. | Lump sum | 1
P36 | UV Disinfection System for Wastewater | Installation of a UV-based wastewater treatment system with a capacity of 10 m³/day. The system includes UV lamps (254 nm wavelength) housed in stainless steel chambers, control panels, and an auto-cleaning mechanism. Includes testing and commissioning to ensure treated water meets WHO discharge standards for biological contamination (<10 CFU/mL). | Lump sum | 1
G54 | Energy-Efficient Smart Lighting Systems | Installation of 60 smart LED light units, each with 20W power and motion sensors for occupancy-based control. Daylight dimmers are integrated for energy efficiency. The system complies with IEC 60598 standards for safety and performance. Includes replacement of old wiring and installation of fire-resistant conduits for safe operation. | Lump sum | 1
S814 | Final Reporting and Closeout | Preparation of as-built drawings (AutoCAD format), detailing all structural, mechanical, and electrical systems. Development of comprehensive O&M manuals for installed systems. Final project report includes challenges faced, resolutions, and compliance certifications. Stakeholder approvals for project handover are included. | Lump sum | 1

## Technical Specs
Rehabilitation and Modernization of Health & Nutrition Centers
This project focuses on the comprehensive rehabilitation and modernization of healthcare centers to enhance functionality, safety, and accessibility for patients and staff. The project addresses critical structural repairs, accessibility upgrades, and improvements in plumbing, electrical, and HVAC systems to ensure compliance with modern safety and operational standards. It also incorporates sustainable and energy-efficient solutions, such as LED smart lighting and solar-powered systems, to reduce operational costs and environmental impact. Special emphasis is placed on the renovation of laboratory and diagnostic areas, the installation of biohazard waste management systems, and the introduction of advanced wastewater treatment solutions to maintain hygiene and environmental compliance. Landscaping and outdoor area improvements aim to provide a welcoming environment for patients and visitors. The project also includes detailed documentation and reporting for compliance and stakeholder engagement, ensuring transparency and accountability. By modernizing these healthcare facilities, the project aims to improve service delivery, enhance patient safety, and create a sustainable and efficient healthcare infrastructure capable of meeting growing demands in Syria and Türkiye.
Ref. | Goods / Services | Description / Specifications | Unit | Quantity
A21 | Wall and Roof Repairs | Walls Restoration (1,500 m²): The restoration will involve applying M20-grade concrete for structural integrity. Before application, surfaces will be cleaned with high-pressure water jets, and cracks will be repaired using epoxy grout injection. A polymer-modified waterproof coating (2 mm thickness) will be applied in two layers to protect the walls from water ingress. The waterproofing process includes priming with epoxy-based primer to enhance adhesion. Roof Sheets Replacement (1,200 m²): Pre-painted galvanized steel sheets (0.5 mm thick) will be installed on a framework of galvanized purlins, supported by rafters spaced at 1.2-meter intervals. A polyethylene vapor barrier will be laid below the sheets to prevent condensation. Fasteners with rubber seals will be used to ensure water-tightness. Roof Truss Reinforcement (15 units): Structural strengthening of trusses will be performed using MS angles (75x75x6 mm) welded or bolted at critical joints. Corrosion-resistant paint will be applied to all steel elements after sanding and priming. Gutters Installation (100 meters): Gutters made of uPVC (150 mm diameter) will be fixed using stainless steel brackets every 500 mm. Downspouts (75 mm diameter) will be installed at specified intervals, ensuring proper water disposal away from the foundation. | Lump sum | 1
U21 | Structural Repairs | Column and Beam Jacketing: 20 columns and 15 beams will be strengthened with M30-grade concrete applied as jacketing with a thickness of 50 mm. The existing concrete surfaces will be roughened by mechanical chipping, followed by the application of bonding agents. Crack Injection: 50 meters of foundation cracks will be filled using high-pressure epoxy injection systems, sealing voids and improving tensile strength. In areas with active reinforcement corrosion, rusted rebar will be replaced with Fe500-grade TMT rebars, ensuring enhanced load-carrying capacity. Beam-Column Connections: Anchoring plates and M12 bolts will be installed at all beam-column joints to enhance rigidity. Post-strengthening, structural integrity will be validated through load testing. | Lump sum | 1
A23 | Accessibility Enhancements | Ramps Construction (5 units): Each ramp, 2 meters wide and 1:12 slope, will be constructed using M20-grade reinforced concrete with non-slip epoxy coating (3 mm thickness). Expansion joints will be provided at intervals to accommodate thermal movement. Handrails Installation (100 meters): Stainless steel handrails (38 mm diameter) will be securely anchored with expansion bolts. Vertical balusters (spaced 100 mm apart) will ensure compliance with accessibility standards. Tactile Paving (150 m²): Raised tactile indicators will be installed on approach paths, guiding visually impaired persons. These will be fixed using polyurethane adhesives over a leveled concrete base. Wheelchair Lifts: Two 500 kg-capacity wheelchair lifts (ISO 9386 compliant) will be installed with electric backup systems. The installation includes pit excavation, reinforced concrete mounting platforms, and integration of control panels with anti-slip buttons. | Lump sum | 1
A22 | Utility System Upgrades | Piping Replacement (200 meters): CPVC (Sch 40) pipes for cold water and insulated PPR pipes (for hot water) will be installed in trenches with a depth of 500 mm. All joints will be solvent-welded, and pressure tests (6 bar) will be conducted to ensure no leaks. Water Tanks Installation: Two 5,000-liter HDPE tanks will be mounted on elevated platforms (1.5 meters high) made of reinforced concrete. Each tank will have inlet and outlet ball valves, overflow protection, and float valves. Electrical Upgrades (80 rooms): Old light fixtures will be replaced with 40W LED lights, offering energy efficiency. The 10-ton split HVAC system will feature R410A refrigerant and include anti-corrosion-treated condenser coils for durability in harsh conditions. | Lump sum | 1
A24 | Interior Refurbishment | Flooring Replacement (2,000 m²): Existing floors will be stripped, and 3 mm anti-bacterial vinyl tiles will be laid over a self-leveling cementitious screed (5 mm thick) to ensure smoothness and adhesion. Painting of Walls (1,800 m²): Walls will be primed with a low-VOC primer before applying two coats of antimicrobial emulsion paint. Surface imperfections will be treated with epoxy fillers. Seating Installation (50 units): Modular seating units will be fabricated with powder-coated steel frames and fire-retardant foam cushions covered in synthetic leather. Door Replacement (15 units): Fire-rated doors (30-minute resistance) made of engineered wood cores will be installed, complete with SS304-grade hinges and lever locks for durability. | Lump sum | 1
P23 | Plumbing Upgrades | Sewer Line Replacement (150 meters): uPVC pipes (200 mm diameter) will be laid in trenches with a slope of 1%. Pipe bedding will consist of 100 mm of sand compacted below the pipe invert. Manholes Construction (5 units): RCC precast manholes (1.2 m diameter, 2 m depth) will be installed with heavy-duty cast iron covers. Septic Tanks Installation (2 units): Prefabricated FRP septic tanks (5 m³ capacity each) will be installed, including inlet/outlet piping and venting. Hydrostatic tests (3 bar) will confirm the integrity of all joints. | Lump sum | 1
P26 | Internal Coatings for Wet Areas | Coating Application (500 m²): The epoxy system includes surface preparation (grinding and degreasing), primer application, and two coats of high-performance epoxy (3 mm thick). Polyurethane joint sealants will ensure flexibility and watertight performance. | Lump sum | 1
A26 | Outdoor Area Improvements | Pathway Resurfacing (200 meters): Concrete tiles (60 mm thick) with anti-slip surfaces will be laid over a 50 mm compacted sand bed and grouted with polymer-modified mortar. Landscaping (500 m²): Native shrubs and drought-resistant grasses will be planted. Drip irrigation systems with timers will be installed for water efficiency. Lighting and Seating: 10 solar-powered LED lights (30W, pole height 6 m) will include pole-mounted battery enclosures. Two steel benches with anti-corrosion paint will be anchored on concrete pads. | Lump sum | 1
A210 | Waste Management Systems | Biohazard Bins (3 units): Color-coded bins (120 L capacity) with leak-proof lids and pedal mechanisms will be installed at key locations. Transportation of 10 tons of debris to certified facilities will include manifests for regulatory compliance. Workers will be provided with PPE kits (gloves, masks, boots) and training on handling hazardous waste. | Lump sum | 1
A28 | Laboratory and Diagnostic Area Upgrade | Flooring Installation (150 m²): Chemical-resistant epoxy flooring (4 mm thick) will be installed. Substrate preparation includes grinding and application of primers. Countertops and Sinks: 10 meters of epoxy-coated steel countertops will include five stainless steel integrated sinks (600 mm x 450 mm) with gooseneck taps. Electrical upgrades include five surge-protected outlets with upgraded earthing. | Lump sum | 1
P36 | UV Disinfection System for Wastewater | System Installation: UV chambers with 254 nm lamps housed in SS304-grade stainless steel units will disinfect 10 m³/day of wastewater. Auto-cleaning mechanisms and flow meters will be included. The system will be tested to meet WHO discharge standards of biological contamination (<10 CFU/mL). | Lump sum | 1
G54 | Energy-Efficient Smart Lighting Systems | Lighting Installation (60 units): Each LED light (20W) will have motion sensors and daylight dimmers. Fire-resistant conduits will be used for wiring, and all installations will comply with IEC 60598 standards. | Lump sum | 1
S814 | Final Reporting and Closeout | Documentation: Preparation of CAD-based as-built drawings detailing all mechanical, electrical, and structural installations. Development of O&M manuals for equipment and systems, highlighting preventive maintenance schedules. Stakeholder approvals will be facilitated with detailed compliance and completion reports. | Lump sum | 1