## BoQ for first 2 years
Establishment of Long Term Arrangement (LTA) for Provision of Rehabilitation and Construction Implementation Services for Education, Health and Nutrition, and WASH Sectors in Türkiye and Syria 6 (2+2+2) years (2025-05/LRPS#9195663) Integrated Water Supply Infrastructure Development Project - First 2 Years
The Integrated Water Supply Infrastructure Development Project aims to provide sustainable and reliable access to clean water for communities through the construction of a comprehensive water supply system. The project involves drilling deep boreholes, installing submersible pumps, constructing reinforced water storage towers and HDPE tanks, laying a 1,000-meter HDPE distribution pipeline, and building tap stations for end-user access. Additionally, it includes solar pumping systems for energy efficiency, drainage channels, and landscaping for environmental sustainability. The initiative is designed to adhere to international standards, ensuring water quality, structural integrity, and long-term operational efficiency.
Ref. | Goods / Services | Description / Specifications | Unit | Quantity | Unit Cost US$ | Unit Cost US$ | Total Cost US$ | Total Cost US$
[5 empty] | Syria | Türkiye | Syria | Türkiye
S111 | Topographical Survey | Conducting detailed topographical surveys using GPS or drones to establish site layout and elevations, including mapping and reporting. | Lump sum | 1
S12 | Land Clearing | Clearing vegetation, shrubs, and topsoil over an area of 2,000 m², including collection, transportation, and proper disposal of debris. | m² | 2000
S132 | Fence Installation | Supply and installation of temporary fencing (barbed wire with posts) to secure a 100-meter perimeter of the project site. | m | 100
S143 | Worker Facilities | Transport and installation of heavy equipment, including borehole drilling rigs and other machinery, with setup and initial calibration. | Lump sum | 1
S144 | Fuel and Lubricants | Establishment of temporary worker shelters, sanitation facilities, and material storage areas, including water and power setup. | Lump sum | 1
S21 | Borehole Drilling | Drilling a borehole to a depth of 150 meters using rotary drilling, including the provision of all necessary drilling fluids. | Meter | 150
S241 | Grouting Pump | Grouting and sealing the borehole using high-grade cement and additives to prevent contamination and stabilize the casing. | m³ | 15
S23 | Supply of Casing Materials | Installation of 150 meters of PVC or steel casing pipes, including joint welding or threading and placement of centralizers. | Meter | 150
S26 | Well Cleaning and Development | Cleaning the borehole using high-pressure airlifting for 10 hours to remove debris, increase yield, and improve water quality. | Hour | 10
S28 | Testing and Quality Control | Comprehensive testing of borehole integrity, including verticality testing, water quality tests, and submission of certified reports. | Lump sum | 1
S311 | Submersible Pump | Supply and installation of a submersible pump suitable for a 150-meter depth, including motor, power cables, and control box. | Unit | 1
S333 | Solar Panel Array | Installation of a complete solar pumping system with 5kW photovoltaic panels, inverter, controller, and mounting structures. | Lump sum | 1
S341 | Portable Generator | Supply and installation of an 8 kW diesel generator for backup power, including wiring and noise insulation measures. | Unit | 1
S351 | Starter Panel | Provision and installation of a control panel with automatic pump starter, circuit breaker, and manual/automatic operation modes. | Unit | 1
S41 | Water Tower | Construction and installation of a 25 m³ reinforced concrete water tower, including ladders, safety railings, and overflow spouts. | Unit | 1
S421 | HDPE Tank | Supply and installation of a 50 m³ UV-resistant HDPE storage tank with fittings, vents, overflow pipes, and cleaning ports. | Unit | 1
S43 | Water Distribution Network | Installation of 1,000 meters of HDPE pipeline, including trenching, backfilling, thrust blocks, and pressure testing. | Meter | 1000
S441 | Platform Construction | Construction of three reinforced concrete tap stations, each with multiple lockable taps, drainage channels, and shading. | Unit | 3
S511 | Concrete Materials | Construction of 100 m² of concrete aprons around the borehole head to prevent spillage, with anti-slip coating and drainage. | m² | 100
S54 | Retaining Walls | Construction of 200 m² of reinforced concrete retaining walls to stabilize slopes and prevent soil erosion. | m² | 200
S55 | Drainage Channels | Installation of 300 meters of open concrete drainage channels to manage surface runoff and prevent flooding. | Meter | 300
S64 | Water Quality Analysis | Water quality analysis, including bacteriological and chemical testing, with reports certified by an accredited laboratory. | Test | 10
S62 | Borehole Yield Testing | Hydrostatic pressure testing of pipelines, including provision of calibrated equipment and submission of compliance certificates. | Lump sum | 1
S281 | Borehole Verticality Testing | Final inspection of the borehole, including video inspection and submission of as-built diagrams and certifications. | Lump sum | 1
S814 | Final Reporting | Preparation of final project documentation, including as-built drawings, O&M manuals, and a detailed project report. | Lump sum | 1
S82 | Demobilization | Demobilization of all equipment and restoration of the site, including debris removal and proper disposal. | Lump sum | 1
S823 | Landscape Restoration | Landscape restoration of 500 m², including grass planting, grading, and soil stabilization to improve site aesthetics. | m² | 500

## BoQ for additional 2 years
Establishment of Long Term Arrangement (LTA) for Provision of Rehabilitation and Construction Implementation Services for Education, Health and Nutrition, and WASH Sectors in Türkiye and Syria 6 (2+2+2) years (2025-05/LRPS#9195663) Integrated Water Supply Infrastructure Development Project - Additional 2 Years
The Integrated Water Supply Infrastructure Development Project aims to provide sustainable and reliable access to clean water for communities through the construction of a comprehensive water supply system. The project involves drilling deep boreholes, installing submersible pumps, constructing reinforced water storage towers and HDPE tanks, laying a 1,000-meter HDPE distribution pipeline, and building tap stations for end-user access. Additionally, it includes solar pumping systems for energy efficiency, drainage channels, and landscaping for environmental sustainability. The initiative is designed to adhere to international standards, ensuring water quality, structural integrity, and long-term operational efficiency.
Ref. | Goods / Services | Description / Specifications | Unit | Quantity | Unit Cost US$ | Unit Cost US$ | Total Cost US$ | Total Cost US$
[5 empty] | Syria | Türkiye | Syria | Türkiye
S111 | Topographical Survey | Conducting detailed topographical surveys using GPS or drones to establish site layout and elevations, including mapping and reporting. | Lump sum | 1
S12 | Land Clearing | Clearing vegetation, shrubs, and topsoil over an area of 2,000 m², including collection, transportation, and proper disposal of debris. | m² | 2000
S132 | Fence Installation | Supply and installation of temporary fencing (barbed wire with posts) to secure a 100-meter perimeter of the project site. | m | 100
S143 | Worker Facilities | Transport and installation of heavy equipment, including borehole drilling rigs and other machinery, with setup and initial calibration. | Lump sum | 1
S144 | Fuel and Lubricants | Establishment of temporary worker shelters, sanitation facilities, and material storage areas, including water and power setup. | Lump sum | 1
S21 | Borehole Drilling | Drilling a borehole to a depth of 150 meters using rotary drilling, including the provision of all necessary drilling fluids. | Meter | 150
S241 | Grouting Pump | Grouting and sealing the borehole using high-grade cement and additives to prevent contamination and stabilize the casing. | m³ | 15
S23 | Supply of Casing Materials | Installation of 150 meters of PVC or steel casing pipes, including joint welding or threading and placement of centralizers. | Meter | 150
S26 | Well Cleaning and Development | Cleaning the borehole using high-pressure airlifting for 10 hours to remove debris, increase yield, and improve water quality. | Hour | 10
S28 | Testing and Quality Control | Comprehensive testing of borehole integrity, including verticality testing, water quality tests, and submission of certified reports. | Lump sum | 1
S311 | Submersible Pump | Supply and installation of a submersible pump suitable for a 150-meter depth, including motor, power cables, and control box. | Unit | 1
S333 | Solar Panel Array | Installation of a complete solar pumping system with 5kW photovoltaic panels, inverter, controller, and mounting structures. | Lump sum | 1
S341 | Portable Generator | Supply and installation of an 8 kW diesel generator for backup power, including wiring and noise insulation measures. | Unit | 1
S351 | Starter Panel | Provision and installation of a control panel with automatic pump starter, circuit breaker, and manual/automatic operation modes. | Unit | 1
S41 | Water Tower | Construction and installation of a 25 m³ reinforced concrete water tower, including ladders, safety railings, and overflow spouts. | Unit | 1
S421 | HDPE Tank | Supply and installation of a 50 m³ UV-resistant HDPE storage tank with fittings, vents, overflow pipes, and cleaning ports. | Unit | 1
S43 | Water Distribution Network | Installation of 1,000 meters of HDPE pipeline, including trenching, backfilling, thrust blocks, and pressure testing. | Meter | 1000
S441 | Platform Construction | Construction of three reinforced concrete tap stations, each with multiple lockable taps, drainage channels, and shading. | Unit | 3
S511 | Concrete Materials | Construction of 100 m² of concrete aprons around the borehole head to prevent spillage, with anti-slip coating and drainage. | m² | 100
S54 | Retaining Walls | Construction of 200 m² of reinforced concrete retaining walls to stabilize slopes and prevent soil erosion. | m² | 200
S55 | Drainage Channels | Installation of 300 meters of open concrete drainage channels to manage surface runoff and prevent flooding. | Meter | 300
S64 | Water Quality Analysis | Water quality analysis, including bacteriological and chemical testing, with reports certified by an accredited laboratory. | Test | 10
S62 | Borehole Yield Testing | Hydrostatic pressure testing of pipelines, including provision of calibrated equipment and submission of compliance certificates. | Lump sum | 1
S281 | Borehole Verticality Testing | Final inspection of the borehole, including video inspection and submission of as-built diagrams and certifications. | Lump sum | 1
S814 | Final Reporting | Preparation of final project documentation, including as-built drawings, O&M manuals, and a detailed project report. | Lump sum | 1
S82 | Demobilization | Demobilization of all equipment and restoration of the site, including debris removal and proper disposal. | Lump sum | 1
S823 | Landscape Restoration | Landscape restoration of 500 m², including grass planting, grading, and soil stabilization to improve site aesthetics. | m² | 500

## BoQ for last 2 years
Establishment of Long Term Arrangement (LTA) for Provision of Rehabilitation and Construction Implementation Services for Education, Health and Nutrition, and WASH Sectors in Türkiye and Syria 6 (2+2+2) years (2025-05/LRPS#9195663) Integrated Water Supply Infrastructure Development Project - Last 2 Years
The Integrated Water Supply Infrastructure Development Project aims to provide sustainable and reliable access to clean water for communities through the construction of a comprehensive water supply system. The project involves drilling deep boreholes, installing submersible pumps, constructing reinforced water storage towers and HDPE tanks, laying a 1,000-meter HDPE distribution pipeline, and building tap stations for end-user access. Additionally, it includes solar pumping systems for energy efficiency, drainage channels, and landscaping for environmental sustainability. The initiative is designed to adhere to international standards, ensuring water quality, structural integrity, and long-term operational efficiency.
Ref. | Goods / Services | Description / Specifications | Unit | Quantity | Unit Cost US$ | Unit Cost US$ | Total Cost US$ | Total Cost US$
[5 empty] | Syria | Türkiye | Syria | Türkiye
S111 | Topographical Survey | Conducting detailed topographical surveys using GPS or drones to establish site layout and elevations, including mapping and reporting. | Lump sum | 1
S12 | Land Clearing | Clearing vegetation, shrubs, and topsoil over an area of 2,000 m², including collection, transportation, and proper disposal of debris. | m² | 2000
S132 | Fence Installation | Supply and installation of temporary fencing (barbed wire with posts) to secure a 100-meter perimeter of the project site. | m | 100
S143 | Worker Facilities | Transport and installation of heavy equipment, including borehole drilling rigs and other machinery, with setup and initial calibration. | Lump sum | 1
S144 | Fuel and Lubricants | Establishment of temporary worker shelters, sanitation facilities, and material storage areas, including water and power setup. | Lump sum | 1
S21 | Borehole Drilling | Drilling a borehole to a depth of 150 meters using rotary drilling, including the provision of all necessary drilling fluids. | Meter | 150
S241 | Grouting Pump | Grouting and sealing the borehole using high-grade cement and additives to prevent contamination and stabilize the casing. | m³ | 15
S23 | Supply of Casing Materials | Installation of 150 meters of PVC or steel casing pipes, including joint welding or threading and placement of centralizers. | Meter | 150
S26 | Well Cleaning and Development | Cleaning the borehole using high-pressure airlifting for 10 hours to remove debris, increase yield, and improve water quality. | Hour | 10
S28 | Testing and Quality Control | Comprehensive testing of borehole integrity, including verticality testing, water quality tests, and submission of certified reports. | Lump sum | 1
S311 | Submersible Pump | Supply and installation of a submersible pump suitable for a 150-meter depth, including motor, power cables, and control box. | Unit | 1
S333 | Solar Panel Array | Installation of a complete solar pumping system with 5kW photovoltaic panels, inverter, controller, and mounting structures. | Lump sum | 1
S341 | Portable Generator | Supply and installation of an 8 kW diesel generator for backup power, including wiring and noise insulation measures. | Unit | 1
S351 | Starter Panel | Provision and installation of a control panel with automatic pump starter, circuit breaker, and manual/automatic operation modes. | Unit | 1
S41 | Water Tower | Construction and installation of a 25 m³ reinforced concrete water tower, including ladders, safety railings, and overflow spouts. | Unit | 1
S421 | HDPE Tank | Supply and installation of a 50 m³ UV-resistant HDPE storage tank with fittings, vents, overflow pipes, and cleaning ports. | Unit | 1
S43 | Water Distribution Network | Installation of 1,000 meters of HDPE pipeline, including trenching, backfilling, thrust blocks, and pressure testing. | Meter | 1000
S441 | Platform Construction | Construction of three reinforced concrete tap stations, each with multiple lockable taps, drainage channels, and shading. | Unit | 3
S511 | Concrete Materials | Construction of 100 m² of concrete aprons around the borehole head to prevent spillage, with anti-slip coating and drainage. | m² | 100
S54 | Retaining Walls | Construction of 200 m² of reinforced concrete retaining walls to stabilize slopes and prevent soil erosion. | m² | 200
S55 | Drainage Channels | Installation of 300 meters of open concrete drainage channels to manage surface runoff and prevent flooding. | Meter | 300
S64 | Water Quality Analysis | Water quality analysis, including bacteriological and chemical testing, with reports certified by an accredited laboratory. | Test | 10
S62 | Borehole Yield Testing | Hydrostatic pressure testing of pipelines, including provision of calibrated equipment and submission of compliance certificates. | Lump sum | 1
S281 | Borehole Verticality Testing | Final inspection of the borehole, including video inspection and submission of as-built diagrams and certifications. | Lump sum | 1
S814 | Final Reporting | Preparation of final project documentation, including as-built drawings, O&M manuals, and a detailed project report. | Lump sum | 1
S82 | Demobilization | Demobilization of all equipment and restoration of the site, including debris removal and proper disposal. | Lump sum | 1
S823 | Landscape Restoration | Landscape restoration of 500 m², including grass planting, grading, and soil stabilization to improve site aesthetics. | m² | 500

## Technical Specs
Integrated Water Supply Infrastructure Development Project
The Integrated Water Supply Infrastructure Development Project aims to provide sustainable and reliable access to clean water for communities through the construction of a comprehensive water supply system. The project involves drilling deep boreholes, installing submersible pumps, constructing reinforced water storage towers and HDPE tanks, laying a 1,000-meter HDPE distribution pipeline, and building tap stations for end-user access. Additionally, it includes solar pumping systems for energy efficiency, drainage channels, and landscaping for environmental sustainability. The initiative is designed to adhere to international standards, ensuring water quality, structural integrity, and long-term operational efficiency.
Ref. | Goods / Services | Description | Unit | Quantity
S111 | Topographical Survey | The topographical survey will involve the use of advanced GPS equipment or drones to establish the site's layout, elevations, and contours. The work includes detailed mapping of natural and artificial features, such as terrain levels, existing structures, roads, and utilities. Deliverables include scaled digital maps, elevation profiles, and georeferenced CAD drawings. The survey must achieve an accuracy of ±10 mm, with all data collected processed through specialized software. The contractor shall also identify key features like low-lying areas and provide recommendations for drainage and site leveling. | Lump sum | 1
S12 | Land Clearing | Land clearing will involve the removal of all vegetation, shrubs, and topsoil over a specified area of 2,000 m². The process includes cutting and uprooting of vegetation, mechanical grading of the area, and proper disposal of debris at designated sites. The cleared topsoil will be stored for possible reuse. Care will be taken to ensure no damage to nearby infrastructure, and activities will comply with environmental regulations. Dust suppression measures, such as water spraying, will be employed during the clearing operations. | m² | 2000
S132 | Fence Installation | The temporary fencing will be constructed using galvanized barbed wire and steel posts to secure the perimeter of the project area. Steel posts, spaced every 2 meters, will be embedded in concrete footings measuring 500 mm deep and 200 mm in diameter. Barbed wire will be tensioned using appropriate anchoring systems to maintain uniform height and avoid sagging. Access points will include lockable gates with provisions for controlled entry and exit. The fencing system will meet local security and safety requirements. | m | 100
S143 | Worker Facilities | Worker facilities will include the transportation, setup, and installation of temporary shelters, sanitation facilities, storage areas, and access to potable water. Sanitation facilities will include portable toilets equipped with handwashing stations. A power supply will be arranged through a combination of generators and solar panels to meet lighting and operational requirements. Worker shelters will be prefabricated units with provisions for ventilation and safety, conforming to local occupational health and safety standards. | Lump sum | 1
S144 | Fuel and Lubricants | The contractor will establish an on-site fuel and lubricant depot, ensuring a consistent supply for machinery and equipment. Diesel fuel will meet ASTM D975 standards, while lubricants will comply with ISO VG 68 specifications for hydraulic systems. Storage tanks will be equipped with secondary containment measures to prevent spills. A log of fuel and lubricant usage will be maintained, and all refueling activities will follow strict safety protocols to prevent contamination or accidents. | Lump sum | 1
S21 | Borehole Drilling | The borehole will be drilled to a depth of 150 meters using a rotary drilling method, with a minimum borehole diameter of 150 mm to accommodate casing and ensure aquifer penetration. Stabilizing drilling fluids such as bentonite or polymer-based muds will be used to maintain borehole integrity and prevent wall collapse. Drilling will involve a minimum of 300 rotations per minute (RPM) with continuous monitoring of torque and penetration rates. Casing pipes will be installed progressively as drilling advances, ensuring proper alignment and stability. A detailed geological log will document soil and rock layers encountered, water strike depths, and drilling progress. The drilling rig must comply with API standards, and all works will adhere to international standards such as ISO 22475-1 for water well drilling. | Meter | 150
S241 | Grouting Pump | The borehole will be grouted using a cement slurry made with Portland cement (Type I/II) and high-performance additives such as superplasticizers and anti-shrinkage agents. The water-to-cement ratio will be 0.5 to achieve optimal viscosity and strength. A high-pressure grouting pump capable of delivering up to 20 liters per minute at a pressure of 15 bar will inject the slurry uniformly into the annular space between the casing and borehole wall. The grouting will extend 10 meters above the aquifer zone to prevent surface water infiltration. The grout will be allowed to cure for a minimum of 24 hours under controlled conditions, with curing monitored to ensure no shrinkage or cracks. | m³ | 15
S23 | Supply of Casing Materials | The casing will consist of 150 meters of PVC or steel pipes, with a wall thickness of at least 5 mm for structural integrity. PVC casings will comply with ISO 4427, while steel casings will conform to ASTM A53 standards. Each joint will be threaded or welded to provide watertight connections, ensuring no leakage under pressure. Centralizers, spaced every 10 meters, will ensure proper centering within the borehole and a consistent annular gap for grouting. End caps and screen sections will be designed to allow controlled water inflow from aquifer zones while preventing debris entry. All materials will be inspected for defects before installation. | Meter | 150
S26 | Well Cleaning and Development | High-pressure airlifting will be performed using a compressor with a minimum capacity of 600 cubic feet per minute (cfm) at 10 bar pressure. The process will inject high-pressure air into the borehole to remove fine sediments, drilling fluids, and debris, thus improving aquifer permeability. The operation will include cyclical pumping and flushing for a minimum of 10 hours or until water clarity meets turbidity standards of less than 5 NTU. Additional development methods such as surging or jetting may be used as needed to enhance water yield and quality. Water flow rates and clarity will be measured periodically during the cleaning process. | Hour | 10
S28 | Testing and Quality Control | Comprehensive testing and quality control measures will be implemented to ensure borehole integrity and functionality. Verticality testing will be conducted using an inclinometer to verify that the deviation does not exceed 1% over the borehole depth. Hydrostatic testing will be carried out on casings to detect leaks, applying 1.5 times the operating pressure. Water samples will be collected at various depths for bacteriological and chemical analysis, adhering to ISO 5667 protocols. Yield testing will assess the sustainable pumping capacity of the borehole, with detailed logs submitted to document findings. Certified laboratories will verify all test results. | Lump sum | 1
S311 | Submersible Pump | The submersible pump will be designed for operation at depths of up to 150 meters, with a minimum discharge capacity of 10 cubic meters per hour (m³/h). The pump will be constructed from corrosion-resistant stainless steel (AISI 316 or equivalent) and include an oil-filled motor rated for continuous duty. Power cables will be of heavy-duty construction with double insulation to withstand underwater conditions, complying with IEC 60245 standards. The pump will be fitted with a non-return valve to prevent backflow and an integrated thermal overload protector. Installation will include proper alignment to minimize vibration and ensure operational efficiency. | Unit | 1
S333 | Solar Panel Array | A solar pumping system will be installed, consisting of 5 kW photovoltaic panels with an efficiency of at least 20%. The panels will be mounted on galvanized steel frames designed to withstand wind speeds of up to 120 km/h, following ASCE 7-16 standards. An inverter and charge controller will manage power conversion and distribution, ensuring smooth operation and minimal energy loss. UV-resistant cabling and weatherproof connectors will be used for electrical connections. The system will be tested under load to verify functionality and ensure uninterrupted operation during peak sunlight hours. | Lump sum | 1
S341 | Portable Generator | An 8 kW diesel generator will be supplied, featuring noise-reduction enclosures to maintain sound levels below 75 dB at a 7-meter distance. The generator will have a fuel efficiency of at least 2.5 liters per hour at 75% load and include a 50-liter fuel tank for extended runtime. Installation will involve proper grounding using copper rods and a dedicated earth pit to meet IEC 60364 standards. The generator will be fitted with an automatic voltage regulator (AVR) to stabilize power output and a manual/automatic transfer switch for seamless backup power transition. | Unit | 1
S351 | Starter Panel | The starter panel will include an automatic pump starter with soft-start functionality to prevent water hammer and reduce power surges. It will also feature MCCBs (Molded Case Circuit Breakers) for circuit protection and digital meters to display voltage, current, and operating status. The enclosure will be weatherproof with an IP65 rating for outdoor use, and internal wiring will use flame-retardant cables. The system will have provisions for both manual and automatic operation, with clear labeling for user convenience. | Unit | 1
S41 | Water Tower | The water tower will be constructed using reinforced concrete to support a 25 m³ storage tank, with a total height of 10 meters from the ground. The foundation will be reinforced with 16 mm diameter rebar at 150 mm spacing, ensuring stability under dynamic loads such as wind and seismic activity. The tower structure will include an access ladder with safety cages, galvanized steel railings, and overflow spouts designed to prevent pooling at the base. The design will meet Eurocode 2 and Eurocode 8 standards for concrete structures and seismic loading. | Unit | 1
S421 | HDPE Tank | The HDPE tank, with a capacity of 50 m³, will be UV-resistant and made from food-grade polyethylene. The tank will include provisions for overflow pipes, cleaning ports, and air vents to maintain pressure equilibrium. It will be installed on a reinforced concrete base, 200 mm thick, with a load-bearing capacity of 10 tons per square meter. Tank fittings will include brass or stainless steel connectors for corrosion resistance. All materials and construction methods will comply with ISO 4427 standards for potable water storage systems. | Unit | 1
S43 | Water Distribution Network | The water distribution network involves the installation of 1,000 meters of HDPE pipes with a nominal diameter of 100 mm and a pressure rating of PN16. The scope includes site preparation, mechanical or manual trench excavation to a minimum depth of 1.2 meters with a width of 500 mm, ensuring frost-free burial and protection against mechanical damage. The trench bottom will be leveled and compacted with a 100 mm layer of sand bedding. HDPE pipes will be jointed using butt fusion welding, with each weld inspected for strength and integrity using non-destructive testing methods. Thrust blocks will be constructed at bends, tees, and other high-pressure zones using M20 grade concrete, with dimensions designed according to the pipeline's pressure and flow characteristics. Backfilling will include layered compaction using vibratory rollers to achieve 95% Proctor density, followed by soil restoration to original ground levels. Pressure testing will involve applying a hydrostatic test pressure of 1.5 times the working pressure for a duration of 24 hours, using calibrated gauges to confirm no leaks. Detailed testing and commissioning reports will be provided. | Meter | 1000
S441 | Platform Construction | The construction of three reinforced concrete tap stations includes a platform area of 3 m² per unit, designed using M25 grade concrete and reinforced with a 150 mm thick slab containing 10 mm diameter rebar spaced at 200 mm centers. The platforms will be finished with a non-slip coating to ensure user safety. Each platform will include multiple lockable brass taps conforming to EN 200 standards, mounted on a GI manifold with anti-corrosion coating. Drainage systems will include 150 mm diameter PVC pipes connected to soak pits, each designed to handle peak wastewater discharge of 0.5 liters per second. Soak pits will be 1.2 meters in diameter and 1.5 meters deep, filled with graded gravel and geotextile layers to ensure infiltration. Shading structures will consist of galvanized steel frames with polycarbonate roofing, designed to withstand wind speeds up to 120 km/h. Accessibility features will include a 1-meter-wide ramp with a slope not exceeding 1:12 to accommodate wheelchair users. | Unit | 3
S511 | Concrete Materials | Concrete aprons surrounding the borehole heads will cover a total area of 100 m², constructed with M25 grade concrete and reinforced with a 10 mm diameter steel rebar mesh at 150 mm spacing in both directions. The aprons will be 100 mm thick, sloped at 2% away from the borehole head to direct water toward designated drainage channels. The edges will be finished with chamfered corners to reduce wear and spalling. An anti-slip epoxy coating conforming to ASTM D4060 standards will be applied to enhance safety. The concrete mix will include admixtures for improved workability and reduced water permeability. All formwork will be properly aligned and oiled to ensure smooth finishes. | m² | 100
S54 | Retaining Walls | Retaining walls will be constructed with M30 grade reinforced concrete, designed to a height of 2.5 meters with a base width of 1 meter. The wall will be reinforced with 12 mm diameter steel bars placed at 150 mm centers in both horizontal and vertical directions. Foundations will be 500 mm deep and 1.5 meters wide, reinforced with 16 mm diameter rebar to prevent settlement. Weep holes, 100 mm in diameter, will be placed every 2 meters horizontally to reduce hydrostatic pressure, and these will be lined with geotextile to prevent soil infiltration. A geotextile fabric layer will also be installed along the rear face of the wall for additional soil stabilization. The wall’s surface will be finished with a cementitious waterproofing coating conforming to EN 1504 standards. | m² | 200
S55 | Drainage Channels | The drainage channels will have a rectangular cross-section, 300 mm wide and 300 mm deep, constructed using M20 grade concrete. A reinforced concrete lining with 8 mm diameter rebar at 200 mm spacing will provide structural integrity. The channels will include a gradient of 1% to ensure effective water flow toward discharge points. Channel surfaces will be finished with a smooth trowel for low hydraulic resistance, and edges will be chamfered for durability. Grated steel covers conforming to ASTM A36 standards will be installed at regular intervals to prevent debris entry while allowing maintenance access. | Meter | 300
S64 | Water Quality Analysis | Water quality testing will include bacteriological tests for total coliforms and E. coli using membrane filtration methods compliant with ISO 9308-1 standards. Chemical analysis will measure pH, turbidity, hardness, nitrates, and heavy metals, including arsenic and lead, using ICP-MS techniques. Sampling will follow strict protocols to prevent contamination, with samples stored in sterile bottles at 4°C and delivered to an ISO 17025-certified laboratory within 6 hours of collection. Each test will include duplicate samples for quality assurance, and results will be documented in a comprehensive report with corrective action recommendations if contaminants exceed permissible levels. | Test | 10
S62 | Borehole Yield Testing | Yield testing will involve step-drawdown and constant-rate pumping tests conducted with a high-capacity submersible pump. The drawdown test will involve increasing discharge rates in three stages, monitoring water level recovery after each stage to assess aquifer performance. The constant-rate test will run for 24 hours, maintaining a steady discharge rate while recording drawdown and recovery data using calibrated piezometers. Hydrostatic pressure testing of pipelines connected to the borehole will be conducted simultaneously, maintaining a pressure 1.5 times the operating pressure for 4 hours to ensure no leaks or pressure drops. Compliance certificates will be issued based on test results. | Lump sum | 1
S281 | Borehole Verticality Testing | Verticality testing will utilize a downhole camera to inspect the alignment of the borehole casing. The camera will provide high-resolution video footage, identifying any deviations from vertical alignment and ensuring the borehole meets specified tolerances of less than 1% deviation over its entire depth. The inspection will also check for obstructions, casing integrity, and proper grouting. A detailed inspection report, including video recordings and annotated diagrams, will be submitted for approval. | Lump sum | 1
S814 | Final Reporting | The final project report will include CAD-based as-built drawings detailing pipeline routes, structural layouts, and borehole designs. Operation and Maintenance (O&M) manuals will provide step-by-step procedures for pump operation, pipeline repairs, and water quality monitoring. The report will also summarize challenges encountered during construction, how they were resolved, and recommendations for future projects. All documents will adhere to donor and stakeholder specifications and will include visual aids such as annotated photos and charts. | Lump sum | 1
S82 | Demobilization | Demobilization will involve the dismantling and removal of all temporary structures, including worker shelters and storage facilities. Heavy machinery will be transported off-site, and all residual debris will be collected and disposed of at licensed facilities. The site will be leveled and compacted, with soil restoration measures applied to mitigate environmental impact. Any areas affected by construction activities will be rehabilitated to their original condition or better. | Lump sum | 1
S823 | Landscape Restoration | Landscape restoration will cover 500 m², focusing on planting drought-resistant grass varieties and native shrubs to improve soil stability and aesthetics. The area will be graded to ensure proper drainage, and bio-engineering measures such as coir mats will be installed on slopes to prevent erosion. A slow-release fertilizer will be applied to promote vegetation growth, and irrigation will be provided as necessary during the establishment period. Soil stabilizers will be incorporated to enhance resilience against erosion, and periodic monitoring will ensure successful plant establishment. | m² | 500